## Note
Air-Conditioning System Information/ Documents
The following form and documents are to be submitted for projects with the provision of air-conditioning system by the appropriate practitioners for Mechanical Works. The completed forms are to be e-signed and submitted as part of the documentary evidences in support of his declaration in the BPD_GM01 or as built GM02 forms along with the BP submission and before TOP application at later stage. In the event that the air-conditioning system information is not available at the time of BP Plan submission, the QP may write in to request for time extension.
Should you need any further clarification, you may contact @
BCA_GM_EFILING_ADMIN@bca.gov.sg | or | BCA_GM_EFILING@bca.gov.sg

## Listing (hide) (hidden)
All the below List has to be editable by Admin (add/remove/rename)
Buidng Work Type | Project Grouping | Building Sub-Catergory | BP/ As-Built
(Select) | (Select) | (Select) | (Select)
Addition to Existing Building | Commercial | Airport services and facilities | BP
Major Retrofitting | Industrial | Academic | As-Built
New Erection | Institutional | Art & Community facilities
Redevelopment | Transit Station | Bus interchange
Reconstruction | Others | Data Centre
Depot
Dormitory
Hawker Centre
Healthcare
Hostel
Hotel
Linkway
Office
Port services and facilities
Production/Manufacturing
Religious Building
Residential
Retail
Service Apartment
Sport
Subway
Transit station
Utility Buildings
Warehouse
Others

## data (hide) (hidden)
Project Reference No.: | Project Description: | Buidng Work Type: | Project Category | GFA (m²): | First Submission date for planning permission (DD/MM/YYY): | Chilled Water System (or both Water Cooled Chilled-Water Plant and Air Cooled Chilled-Water Plant) | Total Air-Conditioned Area (m²): | Total Installed Capacity (RT): e.g.. 2 x 600RT1 x 450RT | Peak Cooling Load (RT): | Design Cooling Load (RT): | Cooling Load Density (W/m²): | Brand: | Water Cooled | Chilled Water Supply Temperature | Chiller Efficiency | Chilled Water Pump Efficiency | Condenser Water Pump Efficiency | Cooling Tower Efficiency | Chiller Plant Efficiency | Air Distribution System Efficiency | Total System Efficiency | Air Cooled | Chilled Water Supply Temperature | Chiller Efficiency | Chilled Water Pump Efficiency | Air Distribution System Efficiency | Total System Efficiency | UNITARY AIR-CONDITIONERS (includes VRF) | Total Air-Conditioned Area (m²): | Total Installed Capacity (RT): | Peak Cooling Load (RT): | Design Cooling Load (RT): | Cooling Load Density (W/m²): | Brand: | Condensing Unit System Efficiency | Air Distribution System Efficiency | Total System Efficiency | WATER-COOLED VRF | Total Air-Conditioned Area (m²): | Total Installed Capacity (RT): | Peak Cooling Load (RT): | Design Cooling Load (RT): | Cooling Load Density (W/m²): | Brand: | Condensing Unit Efficiency | Condenser Water Pump Efficiency | Cooling Tower Efficiency | Package System Efficiency | Air Distribution System Efficiency | Total System Efficiency | Name and Signature of Practitioner for Mechanical Works: | Name and Address of Professional Firm: | Date: | Tel No: | Email Address :
0 | 0 | (Select) | (Select) | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0

## Water-Cooled (2nd-3rd Ed)
Air-Conditioning System Information
For Water Cooled Chilled - Water Plant (For 2nd and 3rd Edition ES Code)
Section A : | General Information
Project Reference No. * (eg A00001-00001-2012)
Submission Type (BP or As-built) * | (Select)
Project Description *
Section A1 : | Water Cooled Chilled- Water Plant
Total Air-con areas | [5 empty] | m2
Expected operating cooling load | [5 empty] | Tons
Expected peak cooling load | [5 empty] | Tons
Design Installed Capacity | [5 empty] | Tons
Cooling load (in W/m2) (i.e. cooling load over air-con areas) | [5 empty] | W/m2
Chiller Configuration / Type | Nos. | Installed Capacity (Tons) |  | Type | Operating/ Standby
Example : | 2 | 800 |  | Centrifugal | Operating
| 1 | 400 |  | Screw | Operating
| 2 | 800 |  | Centrifugal | Standby
Chiller Brand
Cooling Tower Configuration / Type | Nos. | Installed Capacity (Tons) |  | Type | Operating/ Standby
Example : | 2 | 1100 |  | 3 cells axial | Operating
| 1 | 550 |  | 3 cells axial | Operating
| 2 | 1100 |  | 3 cells axial | Standby
Design System Efficiency | Chiller |  |  |  |  | kW/ton
| Chilled Water Pump |  |  |  |  | kW/ton
| Condenser Water Pump |  |  |  |  | kW/ton
| Cooling Tower |  |  |  |  | kW/ton
| Chiller Plant Efficiency |  |  | 0 |  | kW/ton
Chilled Water Pump Head | [5 empty] | m
Condenser Water Pump Head | [5 empty] | m
Section A2 : | Instrumentation for Monitoring Central Water-Cooling Chilled -Water Plant Efficiency
Instrumentation | Requirement |  |  |  | Yes/No
Data Acquisition System | 16 bit resolution
Data Logging | Capability to trend at 1 minute sampling time interval
Flow Meter for Chilled water and condenser water loop | Ultrasonic / Full Bore Magnetic Type
Temperature Sensors | Measurement uncertainty not exceeding ±0.05˚C over entire measurement and calibration range
Dedicated digital power meters | Chillers
Chilled water pumps
Condenser water pumps
Cooling Towers
Overall uncertainty of measurement to be ≤ 5 % of true value
| Errorrms = √ (∑ (UN)2) = |  |  | %
Refer to worked example in Code
Section A3 : | Attached Documentary Evidences
Chiller, pumps, cooling tower | (1) Calculation showing the overall improvement in equipment efficiency of air-conditioning plants which include the design cooling load profile showing the most frequent occurring part load condition (refer to worked example in Code). (2) Technical product information of these equipment. (3) Pump Head Calculations. (4) Plan layouts showing the mode of ventilation for various floors and blocks as well as the location of the plant room and cooling towers.
Instrumentation | (1) Chiller plant room plan layouts showing the locations and types of instrumentation used. (2) Technical specification and product information of all instruments used. (3) Instruments’ calibration certificates from accredited laboratory or equivalent. (4) Summary of instrumentations, standards and measurement accuracy to be presented in stipulated format as mentioned in the Code. (5) Details of the temperature instrumentation measurement to be provided : (a) Configuration of the layout and single line drawing showing how the temperature sensors are connected to the read-out device. (b) Explanation on how the data from the temperature sensors is transferred (e.g. thru’ high level interface, 4-20 mA … etc). (c) Explanation on how the uncertainty of 0.05oC can be achieved for the temperature measurement (Note that it should include all other ancillary instrument and devices that could affect the accuracy of the measurement such as temperature sensors, data logger, digital multi-meter, direct digital controller or programmable logic controller where applicable. Please avoid the use of transmitter unless it is of high accuracy and does not affect the overall accuracy of the temperature measurement). (d) Calibration Reports for all temperature sensors and should be complete with the informations (i) Expanded Uncertainty Value, Confidence Level and Coverage Factor (k value) and interpolation equation where applicable. (e) The Read-Out device or 3rd party software used should have provision to allow for the input of interpolation equation and Constants (A, B, C where applicable) from calibration report of temperature sensors. Please state the provision and arrangement for this project.
I, | , the Practitioner for the Mechanical Works submit the attached information in
support of my declaration of the Design System Efficiency (DSE) of the buliding cooling system and instrumentation
details provided for Project Reference No:
Name and Address of Professional Firm: |  |  | Name and Signature of Practitioner for Mechanical Works:
Date:
Tel No:
Email Address :

## AirCooled_Unitary (2nd-3rd Ed)
Air-Conditioning System Information
For Air-Cooled Chilled Water Plant / Unitary Air-Conditioners (for 2nd and 3rd Edition ES Code)
Section B : | General Information
Project Reference No. * (eg A00001-00001-2012)
Submission Type (BP or As-built) * | (Select)
Project Description *
Section B1 : | Unitary Systems
Total Air-con areas |  |  | m2
Expected operating cooling load |  |  | Tons
Expected peak cooling load |  |  | Tons
Design Installed Capacity |  |  | Tons
Cooling load (in W/m2) (i.e. cooling load over air-con areas) |  |  | W/m2
Design System efficiency * see note |  |  | kW/ton
Brand
* Note : Please take note of the following 1) For water-cooled VRV system, kW/ton include cooling tower fan power. 2) For water-cooled package system, kW/ton include cooling tower fan power and exclude indoor fan power.
Section B2 : | Attached Documentary Evidences
Unitary Systems | (1) Calculation showing the overall improvement in equipment efficiency of air-conditioning plants which include the design cooling profile showing the peak load condition and the most frequently occuring part load condition (refer to worked example in Code). (2) Technical product information of these equipment.
I, | , the Practitioner for the Mechanical Works submit the attached information in
support of my declaration of Design System Efficiency (DSE) of the buliding cooling system and instrumentation
details provided for Project Reference No.:
Name and Address of Professional Firm: |  | Name and Signature of Practitioner for Mechanical Works:
Date:
Tel No:
Email Address :

## All AirCon Type (4th Edition)
SUBMISSION OF DOCUMENTARY EVIDENCES Air-Conditioning System (For 4th Edition ES Code)
Project Reference No.:
Project Description:
| Buidng Work Type: |  | Project Category |  | GFA (m²): |  | First Submission date for planning permission (DD/MM/YYY):
| (Select) |  | (Select)
Chilled Water System (or both Water Cooled Chilled-Water Plant and Air Cooled Chilled-Water Plant)
A/C Main Information
| Total Air-Conditioned Area (m²): |  | Total Installed Capacity (RT): e.g.. 2 x 600RT1 x 450RT |  |  | Peak Cooling Load (RT):
| Design Cooling Load (RT): |  | Cooling Load Density (W/m²): |  |  | Brand:
Design System Efficiency:
| Type of Chilled Water System |  | Water Cooled |  | Air Cooled
| Chilled Water Supply Temperature | [5 empty] | oC
| Chiller Efficiency | [5 empty] | kW/RT
| Chilled Water Pump Efficiency | [5 empty] | kW/RT
| Condenser Water Pump Efficiency | [5 empty] | kW/RT
| Cooling Tower Efficiency | [5 empty] | kW/RT
| Chiller Plant Efficiency |  | 0 |  | 0 |  | kW/RT
| Air Distribution System Efficiency | [5 empty] | kW/RT
| Total System Efficiency |  | 0 |  | 0 |  | kW/RT
UNITARY AIR-CONDITIONERS (includes VRF)
A/C Main Information
| Total Air-Conditioned Area (m²): |  | Total Installed Capacity (RT): |  |  | Peak Cooling Load (RT):
| Design Cooling Load (RT): |  | Cooling Load Density (W/m²): |  |  | Brand:
Design System Efficiency:
| Condensing Unit System Efficiency | [5 empty] | kW/RT
| Air Distribution System Efficiency | [5 empty] | kW/RT
| Total System Efficiency |  | 0 |  |  |  | kW/RT
WATER-COOLED VRF
A/C Main Information
| Total Air-Conditioned Area (m²): |  | Total Installed Capacity (RT): |  |  | Peak Cooling Load (RT):
| Design Cooling Load (RT): |  | Cooling Load Density (W/m²): |  |  | Brand:
Design System Efficiency:
| Condensing Unit Efficiency | [5 empty] | kW/RT
| Condenser Water Pump Efficiency | [5 empty] | kW/RT
| Cooling Tower Efficiency | [5 empty] | kW/RT
| Package System Efficiency |  | 0 |  |  |  | kW/RT
| Air Distribution System Efficiency | [5 empty] | kW/RT
| Total System Efficiency |  | 0 |  |  |  | kW/RT
Note: Require documentary evidence - Refer to the Code for Environmental Sustainability of Buildings, 4th Edition: https://www1-bca-gov-sg-admin.cwp.sg/docs/default-source/docs-corp-buildsg/sustainability/es-code_reg-2008_edition-4-0.pdf
Attached Documentary Evidences
Chiller, pumps, cooling tower |  | (1) Calculation showing the overall improvement in equipment efficiency of air-conditioning plants which include the design cooling load profile showing the most frequent occurring part load condition (refer to worked example in Code). (2) Technical product information of these equipment. (3) Pump Head Calculations. (4) Plan layouts showing the mode of ventilation for various floors and blocks as well as the location of the plant room and cooling towers.
Instrumentation |  | (1) Chiller plant room plan layouts showing the locations and types of instrumentation used. (2) Technical specification and product information of all instruments used. (3) Instruments’ calibration certificates from accredited laboratory or equivalent. (4) Summary of instrumentations, standards and measurement accuracy to be presented in stipulated format as mentioned in the Code. (5) Details of the temperature instrumentation measurement to be provided : (a) Configuration of the layout and single line drawing showing how the temperature sensors are connected to the read-out device. (b) Explanation on how the data from the temperature sensors is transferred (e.g. thru’ high level interface, 4-20 mA … etc). (c) Explanation on how the uncertainty of 0.05oC can be achieved for the temperature measurement (Note that it should include all other ancillary instrument and devices that could affect the accuracy of the measurement such as temperature sensors, data logger, digital multi-meter, direct digital controller or programmable logic controller where applicable. Please avoid the use of transmitter unless it is of high accuracy and does not affect the overall accuracy of the temperature measurement). (d) Calibration Reports for all temperature sensors and should be complete with the informations (i) Expanded Uncertainty Value, Confidence Level and Coverage Factor (k value) and interpolation equation where applicable. (e) The Read-Out device or 3rd party software used should have provision to allow for the input of interpolation equation and Constants (A, B, C where applicable) from calibration report of temperature sensors. Please state the provision and arrangement for this project.
I, |  |  | , the Practitioner for the Mechanical Works submit the attached
information in support of my declaration of the Design System Efficiency (DSE) of the buliding cooling system
and instrumentation details provided for Project Reference No.:
| Name and Address of Professional Firm: |  |  | Name and Signature of Practitioner for Mechanical Works:
Date:
Tel No:
Email Address :